## Grow-In (As -Surveyed MVCD)
Vegetation Report
Name of Line: | WRY2
Voltage: | 230 kV
Weather Case: | As- Surveyed
Wire Condition: | Max Sag FE
Survey Point X (ft) | Survey Point Y (ft) | Survey Point Z (ft) | Back Structure | Ahead Structure | Weather Case | Height above ground (ft) | 3D Radial Distance (ft) (Distance from Conductor)

## Blow-Out (NESC Blowout WSZ)
Vegetation Report
Name of Line: | WRY2
Voltage: | 230 kV
Weather Case: | NESC Blowout (NYPA)
Wire Condition: | Max Sag FE
Survey Point X (ft) | Survey Point Y (ft) | Survey Point Z (ft) | Back Structure | Ahead Structure | Weather Case | Height above ground (ft) | 3D Radial Distance (ft) (Distance from Conductor)
600139.96 | 2208177.41 | 1181.23 | 2/5 | 2/6 | NESC Blowout (RUE 2011) | 52.85 | -0.2
600144.61 | 2208177.93 | 1180.96 | 2/5 | 2/6 | NESC Blowout (RUE 2011) | 50.71 | -5.58
600180.89 | 2208182.06 | 1179.04 | 2/5 | 2/6 | NESC Blowout (RUE 2011) | 48.76 | -2.17
600185.19 | 2208182.56 | 1178.84 | 2/5 | 2/6 | NESC Blowout (RUE 2011) | 52.49 | -6.01
600185.23 | 2208182.57 | 1178.84 | 2/5 | 2/6 | NESC Blowout (RUE 2011) | 50.76 | -4.72
600187.57 | 2208182.84 | 1178.73 | 2/5 | 2/6 | NESC Blowout (RUE 2011) | 47.25 | -0.41
600198.18 | 2208184.09 | 1178.24 | 2/5 | 2/6 | NESC Blowout (RUE 2011) | 51.22 | -3.71
600202.45 | 2208184.59 | 1178.04 | 2/5 | 2/6 | NESC Blowout (RUE 2011) | 49.68 | -0.3
600202.83 | 2208184.64 | 1178.02 | 2/5 | 2/6 | NESC Blowout (RUE 2011) | 45.29 | -1.46
600205.78 | 2208184.99 | 1177.9 | 2/5 | 2/6 | NESC Blowout (RUE 2011) | 52.73 | -2.07
600232.42 | 2208188.2 | 1176.83 | 2/5 | 2/6 | NESC Blowout (RUE 2011) | 52.01 | -1.2
600237.99 | 2208188.88 | 1176.63 | 2/5 | 2/6 | NESC Blowout (RUE 2011) | 50.35 | -0.07
600237.74 | 2208191.28 | 1175.69 | 2/5 | 2/6 | NESC Blowout (RUE 2011)(adj 45.8mph) | 42.08 | -0.07

## Grow-In(CircuitThermal STE WSZ)
Vegetation Report
Name of Line: | WRY2
Voltage: | 230 kV
Weather Case: | STE (RUE 2011)Drake-A
Wire Condition: | Max Sag FE
Survey Point X (ft) | Survey Point Y (ft) | Survey Point Z (ft) | Back Structure | Ahead Structure | Weather Case | Height above ground (ft) | 3D Radial Distance (ft) (Distance from Conductor)

## Fall-In(CircuitThermal STE WSZ)
Vegetation Report
Name of Line: | WRY2
Voltage: | 230 kV
Weather Case: | STE (RUE 2011)Drake-A
Wire Condition: | Max Sag FE
Survey Point X (ft) | Survey Point Y (ft) | Survey Point Z (ft) | Back Structure | Ahead Structure | Weather Case | Height above ground (ft) | 3D Radial Distance (ft) (Distance from Conductor)
591605.91 | 2206923.49 | 1183.25 | 1/1 | 1/2 | Circuit Rating STE (RUE 2011)Drake-A | 46.94 | -1.79
598860.87 | 2207969.42 | 1247.85 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 51.11 | -2.32
598861.21 | 2207970.6 | 1246.11 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 49.45 | -1.61
598864.93 | 2207946.78 | 1269.08 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 71.98 | -2.29
598862.08 | 2207968.82 | 1249.33 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 52.66 | -3.17
598869.56 | 2207946.19 | 1270.95 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 73.96 | -3.08
598872.97 | 2207945.78 | 1273.9 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 76.89 | -5.19
598873.92 | 2207946.36 | 1272.69 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 75.73 | -4.43
598891.68 | 2207988.79 | 1232.4 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 37.75 | -0.25
598902.92 | 2207981.6 | 1246.28 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 51.24 | -6.87
598903.36 | 2207983.43 | 1244.34 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 49.37 | -6.42
598904.23 | 2207981.16 | 1245.98 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 51.01 | -6.08
598908.46 | 2207980.31 | 1243.16 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 48.38 | -2.11
598908.8 | 2207982.64 | 1239.49 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 44.87 | -0.41
598909.56 | 2207988.61 | 1234.37 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 40.33 | -0.25
599804.04 | 2208108 | 1220.75 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.74 | -0.96
599817.1 | 2208096.96 | 1231.05 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.03 | -3.82
599818.86 | 2208095.93 | 1231.88 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.61 | -4.1
599818.61 | 2208103.58 | 1223.25 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.14 | -1.82
599832.4 | 2208098.54 | 1225.02 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.06 | -1.08
599834.2 | 2208108.18 | 1227.41 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.55 | -11.61
599837.28 | 2208101.86 | 1220.52 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.22 | 0
599838.74 | 2208093.78 | 1233.88 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.45 | -6.29
599837.67 | 2208102.54 | 1232.01 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.02 | -12.1
599840.49 | 2208107.15 | 1218.39 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.33 | -2.44
599843.79 | 2208088.95 | 1233.38 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.96 | -2.15
599841.29 | 2208108 | 1220.1 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.18 | -4.8
599842.04 | 2208107.28 | 1225.08 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.36 | -9.33
599842.7 | 2208103.66 | 1223.41 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 72.35 | -4.95
599846.27 | 2208107.38 | 1229.18 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.67 | -13.88
599847.78 | 2208102.25 | 1221.84 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 72.09 | -2.73
599849.53 | 2208093.12 | 1236.27 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 85.01 | -9.56
599847.61 | 2208107.14 | 1227.28 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.26 | -11.95
599849.82 | 2208092.03 | 1237.35 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 85.91 | -9.69
599850.1 | 2208099.97 | 1234.47 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 85.27 | -13.82
599850.75 | 2208099.18 | 1234.83 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 85.77 | -13.62
599851.86 | 2208092.94 | 1231.32 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 81.15 | -4.84
599852.94 | 2208092.8 | 1233.88 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 84.26 | -7.47
599851.97 | 2208106.16 | 1218.75 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.18 | -3.16
599852.87 | 2208102.02 | 1219.97 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 72 | -1.24
599854.63 | 2208094.7 | 1225.31 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 77.01 | -0.87
599855.91 | 2208089.76 | 1230.92 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 82.43 | -2.46
599855.67 | 2208099.28 | 1232.76 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 85.34 | -12.14
599855.24 | 2208103.81 | 1225.38 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.38 | -8.27
599853.7 | 2208114.92 | 1212.94 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.38 | -3.87
599855.32 | 2208106.9 | 1226.3 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.95 | -11.61
599854.58 | 2208113.17 | 1216.26 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.83 | -6.09
599857.42 | 2208096.06 | 1223.74 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.64 | -0.75
599858.45 | 2208092.28 | 1229.45 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 82.16 | -3.41
599858.22 | 2208097.33 | 1232.04 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 85.39 | -10.17
599859.73 | 2208092.66 | 1227.02 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 80.32 | -1.48
599857.22 | 2208110.92 | 1224.56 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.8 | -13.1
599859.14 | 2208103.04 | 1217.93 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 72.18 | -0.64
599858.94 | 2208107.43 | 1221.18 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.57 | -7.37
599859.53 | 2208118.85 | 1209.76 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 66.93 | -3.89
599860.49 | 2208119.11 | 1209.4 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 66.96 | -3.8
599863.9 | 2208097.2 | 1223.38 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.45 | -2.29
599864.74 | 2208101.46 | 1222.85 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.33 | -5.08
599868.66 | 2208097.5 | 1226.3 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 83.85 | -5.89
599870.13 | 2208097.19 | 1225.05 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 82.9 | -4.49
599868.28 | 2208110.69 | 1216.46 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 75.17 | -5.89
599869.38 | 2208103.1 | 1219.01 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 77.21 | -2.96
599871.36 | 2208094.53 | 1223.44 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 81.36 | -0.85
599869.15 | 2208118.37 | 1214.75 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.33 | -9.36
599871.58 | 2208102.99 | 1220.06 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.81 | -4.09
599873.2 | 2208106 | 1222 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 81.66 | -8.46
599874.87 | 2208104.45 | 1224.03 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 83.76 | -9.4
599873.43 | 2208115.39 | 1212.16 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 72.38 | -5.12
599874.83 | 2208113.77 | 1210.02 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.32 | -1.97
599877.08 | 2208106.5 | 1216.32 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.94 | -3.41
599877.18 | 2208111.65 | 1218.72 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.09 | -9.3
599976.25 | 2208133.2 | 1195.59 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 60.08 | -1.77
599977.07 | 2208132.24 | 1195 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.48 | -0.51
600003.74 | 2208125.94 | 1201.4 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64.83 | -1.22
600005.65 | 2208125.89 | 1203.13 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 66.57 | -2.84
600005.81 | 2208125.33 | 1203.43 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 66.88 | -2.7
600051.52 | 2208146.22 | 1187.35 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 51.89 | -0.87
600053.93 | 2208154.41 | 1184.66 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 50.08 | -3.93
600055.02 | 2208149.94 | 1189.19 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 54.44 | -5.42
600055.28 | 2208154.27 | 1182.86 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 48.27 | -2.01
600056.62 | 2208149.21 | 1190.04 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.25 | -5.7
600060.28 | 2208152.01 | 1188.01 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.39 | -5.54
600095.18 | 2208158.98 | 1180.99 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 47.86 | -2.52
600097.19 | 2208150.93 | 1190.5 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 56.67 | -6
600097.88 | 2208149.64 | 1192.08 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 58.31 | -6.6
600096.42 | 2208162.98 | 1176.1 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 43.71 | -0.37
600099.92 | 2208151.5 | 1188.31 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 54.92 | -4.25
600108.16 | 2208151.12 | 1187.42 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 54.55 | -2.82
600108.94 | 2208150.03 | 1186.17 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.26 | -0.69
600134.71 | 2208152.53 | 1184.34 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.66 | -0.02
600134.5 | 2208154.6 | 1188.27 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 57.66 | -5.57
600134.85 | 2208158.18 | 1187.75 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 57.2 | -7.71
600138.32 | 2208146.11 | 1190.77 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 60 | -1.1
600137.42 | 2208159.93 | 1188.7 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 58.35 | -9.85
600140.76 | 2208158.27 | 1191.91 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.82 | -11.75
600141.49 | 2208155.48 | 1196.15 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.96 | -13.83
600140.23 | 2208168.15 | 1191.46 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.5 | -18.44
600142.72 | 2208152.55 | 1197.66 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.44 | -13
600143.44 | 2208152.61 | 1194.28 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64.18 | -9.67
600141.34 | 2208167.72 | 1181.88 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.85 | -8.53
600143.46 | 2208155.7 | 1198.21 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 68.32 | -16.04
600144.87 | 2208160.61 | 1179.48 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 49.71 | -0.89
600145.18 | 2208173.93 | 1179.15 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 50.71 | -9.6
600146.6 | 2208168.84 | 1188.27 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.32 | -15.46
600147.97 | 2208162.89 | 1177.91 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 48.17 | -0.8
600149.11 | 2208160.71 | 1193.78 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64.02 | -15.04
600150.57 | 2208153.55 | 1184.43 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.14 | -0.37
600149.55 | 2208164.26 | 1177.41 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 47.86 | -1.24
600152.14 | 2208147.31 | 1191.06 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.26 | -1.73
600149.72 | 2208164.48 | 1182.53 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.01 | -6.51
600150.21 | 2208164.42 | 1193.13 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.63 | -17.05
600154.16 | 2208145.19 | 1194.6 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64.73 | -3.36
600155.05 | 2208156.41 | 1184.83 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.86 | -2.8
600161.52 | 2208146 | 1194.77 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.62 | -3.93
600162.95 | 2208165.91 | 1179.87 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 51.38 | -4.47
600164.77 | 2208162.49 | 1183.94 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.57 | -6.03
600169 | 2208156.26 | 1190.31 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.93 | -7.43
600170.68 | 2208146.31 | 1197.13 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 68.33 | -5.95
600172.86 | 2208148.85 | 1192.67 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64.16 | -3.53
600172.62 | 2208157.75 | 1187.72 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.54 | -5.81
600173.3 | 2208156.59 | 1188.6 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 60.39 | -5.74
600173.28 | 2208158.79 | 1181.84 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.7 | -0.7
600175.52 | 2208149.66 | 1190.34 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.95 | -1.7
600177.19 | 2208138.09 | 1199.23 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.33 | -0.47
600173.05 | 2208169.03 | 1174.2 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 45.94 | -0.49
600179.35 | 2208168.67 | 1183.25 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.76 | -9.17
600183.7 | 2208161.35 | 1179.81 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.14 | -0.07
600181.91 | 2208174.89 | 1176.07 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 48.76 | -6.06
600186.43 | 2208173.61 | 1186.96 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.79 | -15.93
600185.74 | 2208178.67 | 1179.48 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.49 | -11.71
600185.96 | 2208177.42 | 1177.91 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 50.76 | -9.34
600187.26 | 2208168.62 | 1182.3 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.08 | -7.81
600188.69 | 2208167.23 | 1192.18 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64.94 | -16.6
600188.77 | 2208174.38 | 1174.39 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 47.25 | -3.76
600189.08 | 2208172.45 | 1172.13 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 45.13 | -0.24
600190 | 2208172.05 | 1190.73 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.78 | -18.53
600191.39 | 2208163.08 | 1180.1 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.76 | -1.25
600191.69 | 2208169.58 | 1176.13 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 49.12 | -2.11
600191.86 | 2208170.56 | 1184.53 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 57.58 | -11.2
600191.52 | 2208173.97 | 1192.87 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.87 | -21.86
600193.43 | 2208169.07 | 1194.6 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.55 | -20.1
600194.75 | 2208169.79 | 1182.24 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.16 | -8.16
600199.78 | 2208140.12 | 1199.76 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.67 | -1.04
600196.43 | 2208171.32 | 1192.57 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.69 | -19.52
600196.19 | 2208175.29 | 1188.76 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.25 | -18.51
600195.92 | 2208179.03 | 1188.76 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.98 | -20.83
600199.94 | 2208165.91 | 1187.09 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.79 | -9.78
600199.82 | 2208167.29 | 1190.93 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.68 | -14.67
600201.1 | 2208162.43 | 1182.2 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 54.83 | -2.14
600199.06 | 2208177.87 | 1177.97 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 51.22 | -9.18
600204.81 | 2208141.47 | 1201.2 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 73.32 | -3.28
600205.21 | 2208142.39 | 1199.76 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.95 | -2.63
600203.8 | 2208175.08 | 1176.72 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 49.68 | -5.8
600203.91 | 2208176.72 | 1186.7 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.7 | -16.87
600203.72 | 2208178.36 | 1172.3 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 45.29 | -3.55
600208.79 | 2208148.07 | 1202.54 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 75.19 | -10.17
600205.98 | 2208171.55 | 1183.75 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 56.71 | -10.25
600206.49 | 2208168.4 | 1180.2 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.25 | -4.41
600206.17 | 2208171.06 | 1185.42 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 58.38 | -11.56
600206.91 | 2208168.63 | 1180.43 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.49 | -4.79
600210.2 | 2208147.67 | 1201.86 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.51 | -9.02
600206.87 | 2208177.33 | 1179.64 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.73 | -10.08
600222.9 | 2208152.88 | 1195.06 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.89 | -5.52
600226.11 | 2208157.58 | 1191.91 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.09 | -6.14
600227.73 | 2208165.22 | 1186.99 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 60.5 | -7.35
600230.32 | 2208164.81 | 1184.37 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 57.92 | -4.21
600230.15 | 2208174.62 | 1173.61 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 47.89 | -1.09
600234.07 | 2208155.86 | 1189.26 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.05 | -1.62
600235.74 | 2208159.59 | 1188.99 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.91 | -4.33
600233.66 | 2208179.49 | 1176.86 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.01 | -7.71
600237.66 | 2208157.08 | 1191.13 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.2 | -4.29
600236.53 | 2208170.55 | 1183.61 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 57.73 | -7.58
600239.63 | 2208168.89 | 1179.38 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.54 | -1.86
600239.37 | 2208179.19 | 1174.99 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 50.35 | -5.34
600238.24 | 2208187.76 | 1166.42 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 42.08 | -2.29
600244.01 | 2208164.95 | 1182.37 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 56.77 | -1.49
600243.58 | 2208170.11 | 1185.84 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 60.5 | -9.11
600244.57 | 2208166 | 1187.12 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.55 | -7.03
600245.62 | 2208165.76 | 1181.22 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.71 | -0.88
600246.17 | 2208169.7 | 1179.38 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 54.21 | -2.19
600258.82 | 2208161.09 | 1185.78 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 60.91 | -0.75
600261.5 | 2208153.89 | 1192.28 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.36 | -0.93
600265.81 | 2208156.06 | 1193.88 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.54 | -4.21
600263.96 | 2208169.89 | 1184.2 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 60.32 | -6.14
600263.79 | 2208174.87 | 1186.99 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.23 | -12.77
600264.46 | 2208176.15 | 1186.83 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.31 | -13.57
600265.75 | 2208172.73 | 1180.3 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 56.65 | -4.35
600271.49 | 2208156.22 | 1191.91 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.38 | -1.71
600270.81 | 2208174.67 | 1176.07 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.51 | -1.19
600272.75 | 2208174.43 | 1182.07 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 58.85 | -6.97
600276.58 | 2208162.52 | 1186.07 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.94 | -1.27
600278.07 | 2208164.91 | 1184.43 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.49 | -1.52
600277.35 | 2208170.69 | 1182.14 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.17 | -3.88
600281.95 | 2208177.29 | 1173.8 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.26 | -0.95
600283.29 | 2208175.48 | 1175.41 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 54.99 | -1.16
600307.58 | 2208182.25 | 1170.29 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.56 | -0.03
600321.18 | 2208178.33 | 1174.92 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 58.65 | -0.88
600325.43 | 2208176.73 | 1179.94 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.63 | -3.99
600327.35 | 2208163.49 | 1190.01 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.55 | -2.5
600327.45 | 2208162.83 | 1188.96 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.33 | -0.81
600327.75 | 2208163.88 | 1190.86 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.5 | -3.68
600331.28 | 2208166.22 | 1186.67 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.43 | -1.1
600332.45 | 2208176.39 | 1181.42 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64 | -4.51
600335.9 | 2208182.08 | 1180.3 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64.05 | -7.67
600337.31 | 2208176.1 | 1179.68 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.03 | -2
600339.06 | 2208188.36 | 1168.23 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.74 | -0.17
600355.81 | 2208169.78 | 1186.86 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.58 | -2.44
600385.08 | 2208174.52 | 1183.61 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.92 | -1.68
600386.03 | 2208200.21 | 1165.73 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.18 | -2.2
600391.82 | 2208192.96 | 1172.26 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.07 | -3.55
600392.67 | 2208191.87 | 1170.29 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.11 | -0.78
600440.84 | 2208190.39 | 1176.17 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 66.78 | -1.3
601017.41 | 2208292.97 | 1214.62 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.33 | -5.44
601017.57 | 2208292.38 | 1214.45 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.19 | -5
601016.71 | 2208301.77 | 1208.25 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 68.55 | -2.22
601024.92 | 2208293.15 | 1212.03 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.76 | -1.18
601083.07 | 2208287.05 | 1232.1 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.02 | -0.77
601083.27 | 2208286.49 | 1232.27 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.11 | -0.51
602072.7 | 2208429.91 | 1237.8 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 52.9 | -10.31
602072.89 | 2208429.45 | 1239.27 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 54.36 | -11.36
602072.95 | 2208433.62 | 1234.19 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 49.34 | -9.8
602073.25 | 2208434.83 | 1234.25 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 49.41 | -10.81
602074.41 | 2208436.14 | 1232.19 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 47.33 | -9.66
602075.88 | 2208435.63 | 1227.63 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 42.74 | -4.48
602078.8 | 2208434.76 | 1236.16 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 51.17 | -11.87
602080.74 | 2208434.85 | 1231.04 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 46.18 | -6.63
602118.92 | 2208432.74 | 1233.66 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 48.81 | -2.26
602121.52 | 2208418.03 | 1245.51 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 59.9 | -0.4
602122.28 | 2208418.87 | 1247.28 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 61.6 | -2.77
602122.81 | 2208419.5 | 1248.53 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 62.83 | -4.5
604766.15 | 2208795.8 | 1272.87 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.44 | -2.78
604778.82 | 2208795.3 | 1281.24 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 73.78 | -8.62
604780.23 | 2208789.91 | 1283.27 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 75.76 | -6.23
604780.55 | 2208788.72 | 1281.14 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 73.58 | -3.09
604782.45 | 2208794.55 | 1287.01 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.46 | -13.17
604782.33 | 2208795.57 | 1285.18 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 77.62 | -12.14
604787.98 | 2208792.12 | 1289.93 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 82.01 | -13.13
604787.92 | 2208792.62 | 1289.11 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 81.22 | -12.72
604789.4 | 2208792.54 | 1279.07 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.08 | -2.32
604791.8 | 2208793.22 | 1276.78 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 68.71 | -0.12
604793.9 | 2208787.49 | 1282.81 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.6 | -1.22
604799.25 | 2208787.76 | 1284.52 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.17 | -2.16
604803.59 | 2208799.77 | 1275.01 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 66.79 | -1.19
604804.52 | 2208797.11 | 1281.04 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 72.81 | -5.07
604806.63 | 2208798.08 | 1279.8 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.52 | -4.17
604807.44 | 2208797.42 | 1283.27 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.97 | -7
604807.27 | 2208805.92 | 1278.71 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.16 | -8.57
604814.32 | 2208789.73 | 1287.54 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.86 | -3.97
604814.34 | 2208803.45 | 1285.31 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.71 | -12.15
604817.84 | 2208790.1 | 1287.08 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.32 | -3.14
604817.47 | 2208800.61 | 1280.39 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.62 | -4.55
604817.25 | 2208806.22 | 1287.01 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.11 | -15.21
604818.73 | 2208801.62 | 1281.63 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 72.81 | -6.29
604818.91 | 2208804.67 | 1283.83 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.99 | -10.66
604819.67 | 2208806.07 | 1274.51 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.54 | -2.15
604821.39 | 2208797.3 | 1279.47 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.58 | -0.42
604822.32 | 2208804.61 | 1282.91 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 73.92 | -9.03
604826.63 | 2208800.52 | 1285.34 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.23 | -7.67
604826.84 | 2208808.75 | 1287.83 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 77.86 | -15.75
604827.88 | 2208806.38 | 1283.54 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 73.91 | -9.72
604830.04 | 2208800.82 | 1280.78 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.52 | -2.67
604832.86 | 2208800.38 | 1279.3 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.98 | -0.33
604834.75 | 2208803.65 | 1281.17 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.21 | -4.04
604840.59 | 2208796.85 | 1283.37 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.11 | -0.37
604842.17 | 2208809.58 | 1276.75 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.79 | -2.17
604842.55 | 2208812.27 | 1274.78 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.39 | -1.85
604849.16 | 2208798.67 | 1286.46 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.72 | -3.08
604848.62 | 2208805.63 | 1279.14 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 68.77 | -0.76
604854.39 | 2208799.4 | 1288.33 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.65 | -4.55
604857.21 | 2208810.14 | 1278.62 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.55 | -1.61
604860.96 | 2208806.21 | 1289.64 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.11 | -9.33
604861.79 | 2208803.35 | 1288.16 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 77.86 | -5.7
604865 | 2208802.09 | 1285.96 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 75.49 | -1.92
604867.9 | 2208804.04 | 1284.91 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.11 | -1.64
604868.97 | 2208806.39 | 1283.01 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 72 | -1.16
604878.02 | 2208810.83 | 1281.73 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.45 | -0.9
604878.98 | 2208817.03 | 1287.9 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.88 | -10.87
604879.43 | 2208816.83 | 1285.77 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 72.68 | -8.51
604878.49 | 2208823.1 | 1274.51 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.28 | -1.38
604886.51 | 2208820.82 | 1276.25 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.72 | -0.08
604890.86 | 2208802.26 | 1289.64 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 76.84 | -0.85
604895.16 | 2208806.86 | 1288.43 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.78 | -3.15
604895.26 | 2208807.28 | 1285.05 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 71.35 | -0.08
604896.2 | 2208816.53 | 1279.57 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 65.65 | -1.21
604899.48 | 2208815.33 | 1283.41 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 69.91 | -4.61
605009.7 | 2208798.73 | 1288.23 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 72.78 | -3.76
605010.26 | 2208797.88 | 1290 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.52 | -4.86
605011 | 2208800.73 | 1284.59 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 69.14 | -1.8
605011.7 | 2208797.93 | 1286.16 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 70.62 | -1.12
605014.44 | 2208794.6 | 1294.3 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 78.64 | -6.64
605015.23 | 2208795.42 | 1291.74 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 76.04 | -4.78
605016.1 | 2208793.41 | 1293.18 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 77.44 | -4.59
605024.39 | 2208795.76 | 1288.06 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 71.98 | -1.72
605034.35 | 2208793.04 | 1289.8 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 73.84 | -1.79
605034.88 | 2208793.98 | 1290.2 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.34 | -3.04
605035.93 | 2208794.6 | 1290.3 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.53 | -3.74
605036.85 | 2208793.91 | 1287.97 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 72.2 | -0.89
605044.35 | 2208807.58 | 1276.42 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 59.85 | -0.33
605054.25 | 2208801.31 | 1288.52 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 71.9 | -7.98
605057.37 | 2208801.62 | 1286.88 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 70.13 | -6.68
605057.74 | 2208802.34 | 1284 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 67.17 | -4.36
605058.01 | 2208798.73 | 1295.51 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 78.59 | -12.94
605062.86 | 2208792.11 | 1291.84 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.79 | -3.97
605065.49 | 2208793.21 | 1293.71 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 77 | -7.03
605067.75 | 2208797.59 | 1290.16 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 73.02 | -7.02
605067.93 | 2208794.93 | 1293.18 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 76.17 | -7.92
605071.09 | 2208796.62 | 1284.49 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 67.41 | -0.74
605072.58 | 2208798.12 | 1287.67 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 70.55 | -5.2
605078.35 | 2208796.87 | 1291.77 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.44 | -8.44
605079.84 | 2208795.05 | 1288.98 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 71.44 | -4.12
605080.1 | 2208793.54 | 1292.69 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 75.13 | -6.57
605080.99 | 2208795.11 | 1293.61 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 75.97 | -8.81
605083.91 | 2208799.49 | 1287.01 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 69.49 | -5.98
605095.73 | 2208801.22 | 1284.09 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 66.24 | -4.82
605111.07 | 2208803.33 | 1279.7 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 61.45 | -2.55
605116.53 | 2208795.06 | 1288.16 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 70.15 | -4.6
605118.58 | 2208790.97 | 1289.87 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 71.71 | -2.89
605125.51 | 2208797.36 | 1284.36 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 65.41 | -2.62
605127.46 | 2208794.73 | 1284.82 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 65.76 | -0.92
605129.44 | 2208791.04 | 1293.22 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.36 | -6.38
605130.41 | 2208794.45 | 1286.49 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 67.47 | -2.48
605130.39 | 2208791.33 | 1293.97 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 75.11 | -7.41
605131.33 | 2208788.57 | 1289.8 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 71.11 | -1.01
605134.24 | 2208797.11 | 1282.72 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 63.75 | -1.07
605138.63 | 2208797.22 | 1288.29 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 69.46 | -6.94
605138.63 | 2208796.63 | 1288.06 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 69.24 | -6.23
605142.62 | 2208799.69 | 1281.31 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 62.35 | -2.05
605145.32 | 2208801.18 | 1279.99 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 60.9 | -1.96
605164.82 | 2208797.19 | 1282.36 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 63.41 | -1.74
605166.98 | 2208796.75 | 1281.76 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 62.83 | -0.85
605167.56 | 2208782.83 | 1294.04 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.84 | -1.27
605167.62 | 2208782.27 | 1294.46 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 75.29 | -1.22
605175.95 | 2208797.25 | 1281.9 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 62.67 | -1.52
605178.99 | 2208795.36 | 1283.18 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 64.12 | -1.41
605179.6 | 2208788.5 | 1291.12 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 72.19 | -3.7
605180.39 | 2208789.05 | 1291.94 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 72.95 | -4.98
605184.34 | 2208790.54 | 1289.21 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 69.79 | -3.42
605210.61 | 2208787.59 | 1289.84 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 70.11 | -2.06
605216.01 | 2208795.59 | 1284.75 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 65.07 | -3.73
605229.2 | 2208785.53 | 1290.3 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 70.41 | -1.1
605230.52 | 2208786.15 | 1291.9 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 71.86 | -3.17
591605.91 | 2206923.49 | 1183.25 | 1/1 | 1/2 | Circuit Rating STE (RUE 2011)Drake-A | 46.94 | -2.43
598037.23 | 2207862.81 | 1248.5 | 2/2 | 2/3 | Circuit Rating STE (RUE 2011)Drake-A | 42.53 | -0.64
598860.87 | 2207969.42 | 1247.85 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 51.11 | -3.08
598861.21 | 2207970.6 | 1246.11 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 49.45 | -2.38
598864.93 | 2207946.78 | 1269.08 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 71.98 | -2.84
598862.08 | 2207968.82 | 1249.33 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 52.66 | -3.92
598869.56 | 2207946.19 | 1270.95 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 73.96 | -3.63
598867.13 | 2207978.63 | 1237.71 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 41.56 | -0.47
598872.97 | 2207945.78 | 1273.9 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 76.89 | -5.73
598873.92 | 2207946.36 | 1272.69 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 75.73 | -4.97
598891.68 | 2207988.79 | 1232.4 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 37.75 | -1.24
598902.92 | 2207981.6 | 1246.28 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 51.24 | -7.72
598903.36 | 2207983.43 | 1244.34 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 49.37 | -7.29
598904.23 | 2207981.16 | 1245.98 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 51.01 | -6.91
598908.46 | 2207980.31 | 1243.16 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 48.38 | -2.93
598908.8 | 2207982.64 | 1239.49 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 44.87 | -1.26
598909.56 | 2207988.61 | 1234.37 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 40.33 | -1.2
598937.16 | 2207994.28 | 1231.74 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 38.64 | -0.01
598942.43 | 2207986.64 | 1238.93 | 2/3 | 2/4 | Circuit Rating STE (RUE 2011)Drake-A | 45.36 | -0.22
599804.04 | 2208108 | 1220.75 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.74 | -1.37
599817.1 | 2208096.96 | 1231.05 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.03 | -4.22
599818.86 | 2208095.93 | 1231.88 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.61 | -4.5
599818.61 | 2208103.58 | 1223.25 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.14 | -2.26
599819.34 | 2208104.23 | 1220.75 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.09 | -0.4
599832.4 | 2208098.54 | 1225.02 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.06 | -1.54
599834.2 | 2208108.18 | 1227.41 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.55 | -12.13
599837.28 | 2208101.86 | 1220.52 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.22 | -0.5
599838.74 | 2208093.78 | 1233.88 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.45 | -6.73
599837.67 | 2208102.54 | 1232.01 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.02 | -12.6
599840.49 | 2208107.15 | 1218.39 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.33 | -2.98
599843.79 | 2208088.95 | 1233.38 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.96 | -2.59
599841.29 | 2208108 | 1220.1 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.18 | -5.34
599842.04 | 2208107.28 | 1225.08 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.36 | -9.88
599842.7 | 2208103.66 | 1223.41 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 72.35 | -5.47
599846.27 | 2208107.38 | 1229.18 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.67 | -14.44
599847.78 | 2208102.25 | 1221.84 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 72.09 | -3.27
599849.53 | 2208093.12 | 1236.27 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 85.01 | -10.04
599847.61 | 2208107.14 | 1227.28 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.26 | -12.52
599849.82 | 2208092.03 | 1237.35 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 85.91 | -10.16
599850.1 | 2208099.97 | 1234.47 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 85.27 | -14.35
599850.75 | 2208099.18 | 1234.83 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 85.77 | -14.15
599851.86 | 2208092.94 | 1231.32 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 81.15 | -5.33
599852.94 | 2208092.8 | 1233.88 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 84.26 | -7.97
599851.97 | 2208106.16 | 1218.75 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.18 | -3.74
599852.87 | 2208102.02 | 1219.97 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 72 | -1.79
599854.63 | 2208094.7 | 1225.31 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 77.01 | -1.38
599855.91 | 2208089.76 | 1230.92 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 82.43 | -2.95
599855.67 | 2208099.28 | 1232.76 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 85.34 | -12.68
599855.24 | 2208103.81 | 1225.38 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.38 | -8.84
599853.7 | 2208114.92 | 1212.94 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.38 | -4.5
599855.32 | 2208106.9 | 1226.3 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.95 | -12.2
599854.58 | 2208113.17 | 1216.26 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.83 | -6.72
599857.42 | 2208096.06 | 1223.74 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.64 | -1.28
599858.45 | 2208092.28 | 1229.45 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 82.16 | -3.92
599858.22 | 2208097.33 | 1232.04 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 85.39 | -10.71
599859.73 | 2208092.66 | 1227.02 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 80.32 | -1.99
599857.22 | 2208110.92 | 1224.56 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.8 | -13.72
599856.47 | 2208116.44 | 1207.53 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.23 | -0.43
599859.14 | 2208103.04 | 1217.93 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 72.18 | -1.21
599858.94 | 2208107.43 | 1221.18 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.57 | -7.98
599859.53 | 2208118.85 | 1209.76 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 66.93 | -4.58
599860.49 | 2208119.11 | 1209.4 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 66.96 | -4.49
599863.9 | 2208097.2 | 1223.38 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.45 | -2.85
599864.74 | 2208101.46 | 1222.85 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.33 | -5.67
599866.07 | 2208104.6 | 1215.21 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 72.53 | -0.6
599868.66 | 2208097.5 | 1226.3 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 83.85 | -6.47
599870.13 | 2208097.19 | 1225.05 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 82.9 | -5.07
599868.28 | 2208110.69 | 1216.46 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 75.17 | -6.54
599869.38 | 2208103.1 | 1219.01 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 77.21 | -3.58
599871.36 | 2208094.53 | 1223.44 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 81.36 | -1.42
599869.15 | 2208118.37 | 1214.75 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.33 | -10.07
599871.58 | 2208102.99 | 1220.06 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.81 | -4.71
599873.2 | 2208106 | 1222 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 81.66 | -9.1
599874.87 | 2208104.45 | 1224.03 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 83.76 | -10.04
599873.43 | 2208115.39 | 1212.16 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 72.38 | -5.83
599874.83 | 2208113.77 | 1210.02 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.32 | -2.66
599877.08 | 2208106.5 | 1216.32 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.94 | -4.07
599877.18 | 2208111.65 | 1218.72 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.09 | -9.99
599976.25 | 2208133.2 | 1195.59 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 60.08 | -2.73
599977.07 | 2208132.24 | 1195 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.48 | -1.46
600003.74 | 2208125.94 | 1201.4 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64.83 | -2.1
600005.65 | 2208125.89 | 1203.13 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 66.57 | -3.71
600005.81 | 2208125.33 | 1203.43 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 66.88 | -3.56
600051.52 | 2208146.22 | 1187.35 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 51.89 | -1.94
600053.93 | 2208154.41 | 1184.66 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 50.08 | -5.12
600055.02 | 2208149.94 | 1189.19 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 54.44 | -6.54
600055.28 | 2208154.27 | 1182.86 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 48.27 | -3.2
600056.62 | 2208149.21 | 1190.04 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.25 | -6.82
600060.4 | 2208150.6 | 1183.15 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 48.45 | -0.82
600060.28 | 2208152.01 | 1188.01 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.39 | -6.69
600095.18 | 2208158.98 | 1180.99 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 47.86 | -3.74
600097.19 | 2208150.93 | 1190.5 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 56.67 | -7.1
600097.88 | 2208149.64 | 1192.08 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 58.31 | -7.67
600096.42 | 2208162.98 | 1176.1 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 43.71 | -1.66
600099.92 | 2208151.5 | 1188.31 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 54.92 | -5.35
600108.06 | 2208150.96 | 1183.97 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 51.08 | -0.34
600108.16 | 2208151.12 | 1187.42 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 54.55 | -3.91
600108.94 | 2208150.03 | 1186.17 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.26 | -1.76
600110.33 | 2208157.54 | 1179.48 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 47.25 | -0.87
600134.71 | 2208152.53 | 1184.34 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.66 | -1.13
600134.5 | 2208154.6 | 1188.27 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 57.66 | -6.7
600134.85 | 2208158.18 | 1187.75 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 57.2 | -8.89
600138.32 | 2208146.11 | 1190.77 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 60 | -2.11
600137.42 | 2208159.93 | 1188.7 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 58.35 | -11.06
600140.76 | 2208158.27 | 1191.91 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.82 | -12.93
600141.49 | 2208155.48 | 1196.15 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.96 | -14.97
600140.23 | 2208168.15 | 1191.46 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.5 | -19.79
600142.72 | 2208152.55 | 1197.66 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.44 | -14.1
600143.44 | 2208152.61 | 1194.28 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64.18 | -10.76
600141.34 | 2208167.72 | 1181.88 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.85 | -9.87
600143.46 | 2208155.7 | 1198.21 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 68.32 | -17.18
600144.87 | 2208160.61 | 1179.48 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 49.71 | -2.11
600145.18 | 2208173.93 | 1179.15 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 50.71 | -11.04
600146.6 | 2208168.84 | 1188.27 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.32 | -16.81
600147.97 | 2208162.89 | 1177.91 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 48.17 | -2.04
600149.11 | 2208160.71 | 1193.78 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64.02 | -16.24
600150.57 | 2208153.55 | 1184.43 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.14 | -1.48
600149.55 | 2208164.26 | 1177.41 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 47.86 | -2.5
600152.14 | 2208147.31 | 1191.06 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.26 | -2.75
600149.72 | 2208164.48 | 1182.53 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.01 | -7.78
600150.21 | 2208164.42 | 1193.13 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.63 | -18.32
600154.16 | 2208145.19 | 1194.6 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64.73 | -4.34
600155.05 | 2208156.41 | 1184.83 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.86 | -3.94
600161.52 | 2208146 | 1194.77 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.62 | -4.92
600162.95 | 2208165.91 | 1179.87 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 51.38 | -5.75
600164.77 | 2208162.49 | 1183.94 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.57 | -7.25
600169 | 2208156.26 | 1190.31 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.93 | -8.56
600170.68 | 2208146.31 | 1197.13 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 68.33 | -6.94
600172.86 | 2208148.85 | 1192.67 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64.16 | -4.55
600174.34 | 2208138.87 | 1197.39 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 68.29 | -0.36
600172.62 | 2208157.75 | 1187.72 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.54 | -6.95
600173.3 | 2208156.59 | 1188.6 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 60.39 | -6.86
600173.28 | 2208158.79 | 1181.84 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.7 | -1.86
600175.52 | 2208149.66 | 1190.34 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.95 | -2.73
600177.19 | 2208138.09 | 1199.23 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.33 | -1.36
600176.81 | 2208141.02 | 1195.46 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 66.52 | -0.15
600173.05 | 2208169.03 | 1174.2 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 45.94 | -1.8
600179.35 | 2208168.67 | 1183.25 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.76 | -10.48
600183.7 | 2208161.35 | 1179.81 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.14 | -1.26
600181.91 | 2208174.89 | 1176.07 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 48.76 | -7.47
600186.43 | 2208173.61 | 1186.96 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.79 | -17.32
600185.74 | 2208178.67 | 1179.48 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.49 | -13.18
600185.96 | 2208177.42 | 1177.91 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 50.76 | -10.79
600187.26 | 2208168.62 | 1182.3 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.08 | -9.1
600188.69 | 2208167.23 | 1192.18 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64.94 | -17.87
600188.1 | 2208172.94 | 1170.36 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 43.29 | -0.2
600188.77 | 2208174.38 | 1174.39 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 47.25 | -5.15
600189.08 | 2208172.45 | 1172.13 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 45.13 | -1.6
600190 | 2208172.05 | 1190.73 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.78 | -19.88
600193.4 | 2208148.4 | 1190.18 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.36 | -0.24
600191.39 | 2208163.08 | 1180.1 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.76 | -2.45
600191.69 | 2208169.58 | 1176.13 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 49.12 | -3.42
600191.86 | 2208170.56 | 1184.53 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 57.58 | -12.52
600191.52 | 2208173.97 | 1192.87 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.87 | -23.24
600193.43 | 2208169.07 | 1194.6 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.55 | -21.4
600194.75 | 2208169.79 | 1182.24 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.16 | -9.47
600199.78 | 2208140.12 | 1199.76 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.67 | -1.93
600196.43 | 2208171.32 | 1192.57 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.69 | -20.85
600196.19 | 2208175.29 | 1188.76 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.25 | -19.91
600195.92 | 2208179.03 | 1188.76 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.98 | -22.3
600199.94 | 2208165.91 | 1187.09 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.79 | -11.01
600199.82 | 2208167.29 | 1190.93 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.68 | -15.92
600201.1 | 2208162.43 | 1182.2 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 54.83 | -3.31
600199.06 | 2208177.87 | 1177.97 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 51.22 | -10.62
600204.81 | 2208141.47 | 1201.2 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 73.32 | -4.18
600205.21 | 2208142.39 | 1199.76 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.95 | -3.54
600202.98 | 2208169.37 | 1173.97 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 46.89 | -0.36
600205.98 | 2208150.98 | 1189.39 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.06 | -0.74
600203.8 | 2208175.08 | 1176.72 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 49.68 | -7.17
600203.91 | 2208176.72 | 1186.7 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.7 | -18.28
600203.72 | 2208178.36 | 1172.3 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 45.29 | -4.98
600205.98 | 2208166.57 | 1176.07 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 49.14 | -0.2
600208.79 | 2208148.07 | 1202.54 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 75.19 | -11.14
600205.98 | 2208171.55 | 1183.75 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 56.71 | -11.56
600206.49 | 2208168.4 | 1180.2 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.25 | -5.67
600206.17 | 2208171.06 | 1185.42 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 58.38 | -12.86
600206.91 | 2208168.63 | 1180.43 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.49 | -6.05
600210.2 | 2208147.67 | 1201.86 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.51 | -9.99
600206.87 | 2208177.33 | 1179.64 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.73 | -11.49
600215.17 | 2208139.99 | 1199.46 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.59 | -0.1
600222.9 | 2208152.88 | 1195.06 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.89 | -6.52
600226.11 | 2208157.58 | 1191.91 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.09 | -7.2
600227.73 | 2208165.22 | 1186.99 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 60.5 | -8.52
600230.32 | 2208164.81 | 1184.37 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 57.92 | -5.37
600230.15 | 2208174.62 | 1173.61 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 47.89 | -2.42
600234.07 | 2208155.86 | 1189.26 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.05 | -2.66
600235.61 | 2208149.45 | 1192.47 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.89 | -0.05
600235.74 | 2208159.59 | 1188.99 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.91 | -5.41
600233.66 | 2208179.49 | 1176.86 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.01 | -9.13
600237.66 | 2208157.08 | 1191.13 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.2 | -5.35
600236.53 | 2208170.55 | 1183.61 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 57.73 | -8.83
600239.63 | 2208168.89 | 1179.38 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.54 | -3.07
600239.37 | 2208179.19 | 1174.99 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 50.35 | -6.74
600238.24 | 2208187.76 | 1166.42 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 42.08 | -3.86
600244.01 | 2208164.95 | 1182.37 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 56.77 | -2.64
600243.58 | 2208170.11 | 1185.84 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 60.5 | -10.34
600244.57 | 2208166 | 1187.12 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.55 | -8.2
600242.97 | 2208178.45 | 1169.97 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 45.39 | -0.98
600245.62 | 2208165.76 | 1181.22 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.71 | -2.04
600246.17 | 2208169.7 | 1179.38 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 54.21 | -3.41
600247.35 | 2208180.72 | 1168.26 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 44.19 | -0.7
600253.08 | 2208161.42 | 1184.14 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.12 | -0.94
600258.82 | 2208161.09 | 1185.78 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 60.91 | -1.83
600261.5 | 2208153.89 | 1192.28 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.36 | -1.92
600265.81 | 2208156.06 | 1193.88 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.54 | -5.23
600263.96 | 2208169.89 | 1184.2 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 60.32 | -7.35
600263.79 | 2208174.87 | 1186.99 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.23 | -14.06
600267.09 | 2208156.8 | 1188.63 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64.38 | -0.53
600264.46 | 2208176.15 | 1186.83 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.31 | -14.89
600265.75 | 2208172.73 | 1180.3 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 56.65 | -5.6
600270.99 | 2208155.44 | 1190.5 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.81 | -0.61
600271.49 | 2208156.22 | 1191.91 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.38 | -2.72
600270.81 | 2208174.67 | 1176.07 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.51 | -2.47
600272.75 | 2208174.43 | 1182.07 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 58.85 | -8.25
600276.58 | 2208162.52 | 1186.07 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.94 | -2.37
600278.07 | 2208164.91 | 1184.43 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.49 | -2.65
600277.35 | 2208170.69 | 1182.14 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.17 | -5.09
600279.46 | 2208171.27 | 1177.64 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.21 | -1.07
600281.95 | 2208177.29 | 1173.8 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.26 | -2.3
600283.29 | 2208175.48 | 1175.41 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 54.99 | -2.48
600285.16 | 2208170.57 | 1177.18 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 56.72 | -0.3
600307.58 | 2208182.25 | 1170.29 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.56 | -1.46
600321.18 | 2208178.33 | 1174.92 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 58.65 | -2.23
600325.43 | 2208176.73 | 1179.94 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.63 | -5.29
600327.35 | 2208163.49 | 1190.01 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.55 | -3.59
600327.45 | 2208162.83 | 1188.96 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.33 | -1.89
600327.75 | 2208163.88 | 1190.86 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.5 | -4.77
600324.39 | 2208188.12 | 1166.82 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 51.93 | -1.18
600327.26 | 2208174.78 | 1176.86 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.13 | -0.37
600331.28 | 2208166.22 | 1186.67 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.43 | -2.22
600332.45 | 2208176.39 | 1181.42 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64 | -5.8
600333.09 | 2208183.73 | 1170.16 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 54.37 | -0.52
600335.9 | 2208182.08 | 1180.3 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 64.05 | -9.06
600337.31 | 2208176.1 | 1179.68 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.03 | -3.26
600338.5 | 2208187.84 | 1167.7 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.03 | -0.79
600339.06 | 2208188.36 | 1168.23 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.74 | -1.67
600351.38 | 2208158.65 | 1193.59 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.79 | -0.68
600355.81 | 2208169.78 | 1186.86 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.58 | -3.6
600385.08 | 2208174.52 | 1183.61 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.92 | -2.92
600385.46 | 2208198.93 | 1162.62 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.12 | -0.02
600386.03 | 2208200.21 | 1165.73 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 55.18 | -3.84
600391.51 | 2208190.59 | 1169.05 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 57.79 | -0.24
600391.82 | 2208192.96 | 1172.26 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.07 | -5.07
600392.67 | 2208191.87 | 1170.29 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 59.11 | -2.27
600396.2 | 2208200.08 | 1162.68 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 52.77 | -0.01
600440.84 | 2208190.39 | 1176.17 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 66.78 | -2.7
600471.01 | 2208204.22 | 1167.87 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 58.3 | -0.72
601017.41 | 2208292.97 | 1214.62 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.33 | -6
601017.57 | 2208292.38 | 1214.45 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.19 | -5.56
601016.71 | 2208301.77 | 1208.25 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 68.55 | -2.81
601024.92 | 2208293.15 | 1212.03 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.76 | -1.71
601083.07 | 2208287.05 | 1232.1 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.02 | -1
601083.27 | 2208286.49 | 1232.27 | 2/5 | 2/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.11 | -0.74
602072.7 | 2208429.91 | 1237.8 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 52.9 | -11.06
602072.89 | 2208429.45 | 1239.27 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 54.36 | -12.1
602072.95 | 2208433.62 | 1234.19 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 49.34 | -10.59
602073.25 | 2208434.83 | 1234.25 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 49.41 | -11.62
602074.41 | 2208436.14 | 1232.19 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 47.33 | -10.48
602075.88 | 2208435.63 | 1227.63 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 42.74 | -5.29
602078.8 | 2208434.76 | 1236.16 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 51.17 | -12.66
602080.74 | 2208434.85 | 1231.04 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 46.18 | -7.42
602118.92 | 2208432.74 | 1233.66 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 48.81 | -2.94
602121.52 | 2208418.03 | 1245.51 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 59.9 | -0.93
602122.28 | 2208418.87 | 1247.28 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 61.6 | -3.32
602122.81 | 2208419.5 | 1248.53 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 62.83 | -5.05
602133.23 | 2208422.75 | 1241.73 | 3/1 | 3/2 | Circuit Rating STE (RUE 2011)Drake-A | 56.73 | -0.07
604104.76 | 2208705.53 | 1259.91 | 3/4 | 3/5 | Circuit Rating STE (RUE 2011)Drake-A | 60.93 | -0.34
604666.39 | 2208769.77 | 1274.12 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 68.33 | -0.18
604667.31 | 2208769.67 | 1274.42 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 68.6 | -0.24
604694.8 | 2208777.93 | 1271.92 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.67 | -0.3
604766.15 | 2208795.8 | 1272.87 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.44 | -3.37
604778.82 | 2208795.3 | 1281.24 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 73.78 | -9.16
604780.23 | 2208789.91 | 1283.27 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 75.76 | -6.74
604780.55 | 2208788.72 | 1281.14 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 73.58 | -3.59
604782.45 | 2208794.55 | 1287.01 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.46 | -13.69
604782.33 | 2208795.57 | 1285.18 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 77.62 | -12.66
604782.7 | 2208797.83 | 1271.23 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.63 | -0.34
604787.98 | 2208792.12 | 1289.93 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 82.01 | -13.62
604787.92 | 2208792.62 | 1289.11 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 81.22 | -13.21
604789.4 | 2208792.54 | 1279.07 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.08 | -2.81
604791.8 | 2208793.22 | 1276.78 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 68.71 | -0.59
604793.9 | 2208787.49 | 1282.81 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.6 | -1.67
604799.25 | 2208787.76 | 1284.52 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.17 | -2.59
604803.59 | 2208799.77 | 1275.01 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 66.79 | -1.65
604804.52 | 2208797.11 | 1281.04 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 72.81 | -5.51
604806.63 | 2208798.08 | 1279.8 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.52 | -4.61
604807.44 | 2208797.42 | 1283.27 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.97 | -7.42
604807.27 | 2208805.92 | 1278.71 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.16 | -9.03
604814.32 | 2208789.73 | 1287.54 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.86 | -4.34
604814.34 | 2208803.45 | 1285.31 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.71 | -12.57
604817.84 | 2208790.1 | 1287.08 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.32 | -3.5
604817.47 | 2208800.61 | 1280.39 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.62 | -4.94
604817.25 | 2208806.22 | 1287.01 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.11 | -15.62
604818.73 | 2208801.62 | 1281.63 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 72.81 | -6.68
604818.91 | 2208804.67 | 1283.83 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.99 | -11.06
604819.67 | 2208806.07 | 1274.51 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.54 | -2.55
604821.39 | 2208797.3 | 1279.47 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 70.58 | -0.78
604822.32 | 2208804.61 | 1282.91 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 73.92 | -9.42
604826.63 | 2208800.52 | 1285.34 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.23 | -8.02
604826.84 | 2208808.75 | 1287.83 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 77.86 | -16.12
604827.88 | 2208806.38 | 1283.54 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 73.91 | -10.08
604830.04 | 2208800.82 | 1280.78 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.52 | -3
604830.35 | 2208802.5 | 1276.94 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.62 | -0.32
604832.86 | 2208800.38 | 1279.3 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.98 | -0.65
604834.75 | 2208803.65 | 1281.17 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 71.21 | -4.36
604840.59 | 2208796.85 | 1283.37 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.11 | -0.64
604842.17 | 2208809.58 | 1276.75 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 65.79 | -2.46
604842.55 | 2208812.27 | 1274.78 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 63.39 | -2.15
604849.16 | 2208798.67 | 1286.46 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 76.72 | -3.32
604848.62 | 2208805.63 | 1279.14 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 68.77 | -1.01
604854.39 | 2208799.4 | 1288.33 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 78.65 | -4.76
604857.21 | 2208810.14 | 1278.62 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 67.55 | -1.82
604860.96 | 2208806.21 | 1289.64 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 79.11 | -9.51
604861.79 | 2208803.35 | 1288.16 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 77.86 | -5.88
604865 | 2208802.09 | 1285.96 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 75.49 | -2.08
604867.9 | 2208804.04 | 1284.91 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.11 | -1.78
604868.97 | 2208806.39 | 1283.01 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 72 | -1.3
604878.02 | 2208810.83 | 1281.73 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 69.45 | -0.98
604878.98 | 2208817.03 | 1287.9 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 74.88 | -10.95
604879.43 | 2208816.83 | 1285.77 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 72.68 | -8.58
604878.49 | 2208823.1 | 1274.51 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 61.28 | -1.46
604886.51 | 2208820.82 | 1276.25 | 3/5 | 3/6 | Circuit Rating STE (RUE 2011)Drake-A | 62.72 | -0.11
604890.86 | 2208802.26 | 1289.64 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 76.84 | -0.89
604895.16 | 2208806.86 | 1288.43 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.78 | -3.21
604895.26 | 2208807.28 | 1285.05 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 71.35 | -0.14
604896.2 | 2208816.53 | 1279.57 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 65.65 | -1.28
604899.48 | 2208815.33 | 1283.41 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 69.91 | -4.69
604900.16 | 2208808.6 | 1283.6 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 69.81 | -0.05
605009.7 | 2208798.73 | 1288.23 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 72.78 | -4.15
605010.26 | 2208797.88 | 1290 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.52 | -5.25
605011 | 2208800.73 | 1284.59 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 69.14 | -2.2
605011.7 | 2208797.93 | 1286.16 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 70.62 | -1.51
605014.44 | 2208794.6 | 1294.3 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 78.64 | -7.02
605015.23 | 2208795.42 | 1291.74 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 76.04 | -5.17
605016.1 | 2208793.41 | 1293.18 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 77.44 | -4.98
605024.39 | 2208795.76 | 1288.06 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 71.98 | -2.12
605034.35 | 2208793.04 | 1289.8 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 73.84 | -2.2
605034.88 | 2208793.98 | 1290.2 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.34 | -3.46
605035.93 | 2208794.6 | 1290.3 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.53 | -4.17
605036.85 | 2208793.91 | 1287.97 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 72.2 | -1.31
605044.35 | 2208807.58 | 1276.42 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 59.85 | -0.83
605054.25 | 2208801.31 | 1288.52 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 71.9 | -8.46
605057.37 | 2208801.62 | 1286.88 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 70.13 | -7.17
605057.74 | 2208802.34 | 1284 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 67.17 | -4.85
605058.01 | 2208798.73 | 1295.51 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 78.59 | -13.42
605062.86 | 2208792.11 | 1291.84 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.79 | -4.41
605065.49 | 2208793.21 | 1293.71 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 77 | -7.49
605067.75 | 2208797.59 | 1290.16 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 73.02 | -7.5
605067.93 | 2208794.93 | 1293.18 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 76.17 | -8.39
605071.09 | 2208796.62 | 1284.49 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 67.41 | -1.22
605072.58 | 2208798.12 | 1287.67 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 70.55 | -5.69
605078.35 | 2208796.87 | 1291.77 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.44 | -8.93
605079.84 | 2208795.05 | 1288.98 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 71.44 | -4.6
605080.1 | 2208793.54 | 1292.69 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 75.13 | -7.04
605080.99 | 2208795.11 | 1293.61 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 75.97 | -9.29
605083.91 | 2208799.49 | 1287.01 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 69.49 | -6.49
605095.73 | 2208801.22 | 1284.09 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 66.24 | -5.35
605101.46 | 2208797.74 | 1281.76 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 63.8 | -0.36
605103.6 | 2208794.41 | 1284.13 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 66.25 | -0.08
605111.07 | 2208803.33 | 1279.7 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 61.45 | -3.11
605116.53 | 2208795.06 | 1288.16 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 70.15 | -5.11
605118.58 | 2208790.97 | 1289.87 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 71.71 | -3.39
605125.51 | 2208797.36 | 1284.36 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 65.41 | -3.15
605127.46 | 2208794.73 | 1284.82 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 65.76 | -1.43
605129.44 | 2208791.04 | 1293.22 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.36 | -6.87
605130.41 | 2208794.45 | 1286.49 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 67.47 | -2.99
605130.39 | 2208791.33 | 1293.97 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 75.11 | -7.91
605131.33 | 2208788.57 | 1289.8 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 71.11 | -1.49
605134.24 | 2208797.11 | 1282.72 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 63.75 | -1.6
605138.63 | 2208797.22 | 1288.29 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 69.46 | -7.48
605138.63 | 2208796.63 | 1288.06 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 69.24 | -6.76
605142.62 | 2208799.69 | 1281.31 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 62.35 | -2.6
605145.32 | 2208801.18 | 1279.99 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 60.9 | -2.53
605160.56 | 2208797.71 | 1280.22 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 61.15 | -0.4
605164.82 | 2208797.19 | 1282.36 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 63.41 | -2.29
605166.98 | 2208796.75 | 1281.76 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 62.83 | -1.4
605167.56 | 2208782.83 | 1294.04 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.84 | -1.74
605167.62 | 2208782.27 | 1294.46 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 75.29 | -1.69
605175.95 | 2208797.25 | 1281.9 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 62.67 | -2.07
605178.99 | 2208795.36 | 1283.18 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 64.12 | -1.95
605179.6 | 2208788.5 | 1291.12 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 72.19 | -4.21
605180.39 | 2208789.05 | 1291.94 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 72.95 | -5.49
605184.34 | 2208790.54 | 1289.21 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 69.79 | -3.93
605190.55 | 2208792.24 | 1283.64 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 64.52 | -0.08
605210.61 | 2208787.59 | 1289.84 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 70.11 | -2.55
605216.01 | 2208795.59 | 1284.75 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 65.07 | -4.27
605229.2 | 2208785.53 | 1290.3 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 70.41 | -1.57
605230.52 | 2208786.15 | 1291.9 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 71.86 | -3.65
605231.07 | 2208789.69 | 1293.51 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 73.08 | -8.08
605231.19 | 2208789.23 | 1295.28 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.83 | -9.46
605231.94 | 2208787.95 | 1295.77 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 75.35 | -8.9
605233.15 | 2208792.07 | 1286.19 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 65.77 | -2.79
605255.53 | 2208780.98 | 1293.35 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 72.63 | -0.78
605258.31 | 2208779.38 | 1295.05 | 3/6 | 3/7 | Circuit Rating STE (RUE 2011)Drake-A | 74.18 | -1.07
605974.29 | 2208770.21 | 1299.9 | 3/7 | 3/8 | Circuit Rating STE (RUE 2011)Drake-A | 44.86 | -2.35
605974.68 | 2208771.03 | 1298.59 | 3/7 | 3/8 | Circuit Rating STE (RUE 2011)Drake-A | 43.56 | -1.77
617220.83 | 2208197.92 | 1346.66 | 5/7 | 6/1 | Circuit Rating STE (RUE 2011)Drake-A | 52.98 | -0.05
617241.86 | 2208176.36 | 1364.41 | 5/7 | 6/1 | Circuit Rating STE (RUE 2011)Drake-A | 69.5 | -1.01
617244.52 | 2208170.8 | 1371.4 | 5/7 | 6/1 | Circuit Rating STE (RUE 2011)Drake-A | 76.14 | -3.19
617244.54 | 2208169.62 | 1370.97 | 5/7 | 6/1 | Circuit Rating STE (RUE 2011)Drake-A | 75.67 | -1.72
617244.8 | 2208174.01 | 1367.59 | 5/7 | 6/1 | Circuit Rating STE (RUE 2011)Drake-A | 72.21 | -2.08
617245.15 | 2208172.37 | 1367.79 | 5/7 | 6/1 | Circuit Rating STE (RUE 2011)Drake-A | 72.39 | -0.89
620245.53 | 2208038.47 | 1378.71 | 6/4 | 6/5 | Circuit Rating STE (RUE 2011)Drake-A | 52.28 | -5.36
620246.2 | 2208040.24 | 1377.33 | 6/4 | 6/5 | Circuit Rating STE (RUE 2011)Drake-A | 51.16 | -5.76
620246.32 | 2208039.15 | 1379.11 | 6/4 | 6/5 | Circuit Rating STE (RUE 2011)Drake-A | 52.74 | -6.45
620749.51 | 2208018.63 | 1378.78 | 6/5 | 6/6 | Circuit Rating STE (RUE 2011)Drake-A | 45.72 | -1.42
620751.64 | 2208013.17 | 1384.35 | 6/5 | 6/6 | Circuit Rating STE (RUE 2011)Drake-A | 50.73 | -2.14
620751.81 | 2208012.71 | 1386.68 | 6/5 | 6/6 | Circuit Rating STE (RUE 2011)Drake-A | 53.04 | -4.07
621676.5 | 2207967.11 | 1388.52 | 6/6 | 6/7 | Circuit Rating STE (RUE 2011)Drake-A | 50.04 | -2.15
621696.89 | 2207962.65 | 1392.66 | 6/6 | 6/7 | Circuit Rating STE (RUE 2011)Drake-A | 54.34 | -3.39
621697.48 | 2207962.71 | 1391.01 | 6/6 | 6/7 | Circuit Rating STE (RUE 2011)Drake-A | 52.68 | -1.81